## Build Fixture Count
Facility Name | Constr. Complete | Building Gross Sq. Ft | Building Fixture Count | Total Construction Cost | Building Net Sq. Ft | Old Watts | Old W/s.f. (fluor. only) | New Watts | New W/s.f. (fluor. only) | Watt Reduction | ICECF Grant @ $.60/W | Annual Cost Savings (12h/day) | Annual kWh Savings | Net Cost after ICECF | Notes
RAL | 2010-04-27 | 279832 | 2064 | 114769 | 89901 | 165152 | 1.837 | 129134 | 1.4364 | 36018 | 21610.8 | 11831.913 | 157758.84 | 93158.2 | remainder; 242 were on ICECF '08 grant
Med Sci | 2011-03-01 | 114781 | 2195 | 479054 | 97169 | 195830 | 2.0154 | 100728 | 1.0366 | 95102 | 57061.2 | 31241.007 | 416546.76 | 421992.8 | Includes DM ceiling repair/replacements
Undergrad Lib | 2010-04-09 | 95905 | 2294 | 116274 | 59643 | 197691 | 3.3146 | 65151 | 1.0923 | 132540 | 79524 | 43539.39 | 580525.2 | 36750
Greg Hall - capital project | 2011-04-15 | 110755 | 426 | 0 | 37455 | 35686 | 0.95277 | 20885 | 0.5576 | 14801 | 8880.6 | 4862.1285 | 64828.38 | -8880.6 | 777 T12 fixtures remain to be done
DKH - capital project | 2011-04-15 | 81018 | 858 | 0 | 63385 | 90096 | 1.4214 | 70867 | 1.118 | 19229 | 11537.4 | 6316.7265 | 84223.02 | -11537.4 | 54 T12 fixtures remain to be done
Morrill - capital project | 2011-04-15 | 170125 | 195 | 0 | 15493 | 15624 | 1.0085 | 9738 | 0.62854 | 5886 | 3531.6 | 1933.551 | 25780.68 | -3531.6 | 2,594 fixtures remain to be done
Lincoln - capital project | 2011-04-15 |  | 1787 | 0 | 143119 | 151770 | 1.0604 | 128965 | 0.9011 | 22805 | 13683 | 7491.4425 | 99885.9 | -13683
PPSB | 2011-04-09 | 162881 | 1728 | 97459.2 | 139852 | 229851 | 1.6435 | 164886 | 1.179 | 64965 | 38979 | 21341.0025 | 284546.7 | 58480.2
DCL | 2011-03-31 | 65000 | 2793 | 157525.2 | 146516 | 256542 | 1.7509 | 160014 | 1.0921 | 96528 | 57916.8 | 31709.448 | 422792.64 | 99608.4
CSL | 2011-03-29 | 124005 | 1903 | 107329.2 | 118927 | 160418 | 1.3489 | 92856 | 0.78078 | 67562 | 40537.2 | 22194.117 | 295921.56 | 66792
108 - CAB | 2011-02-15 | 41970 | 621 | 38009 | 30302 | 52596 | 1.7357 | 26629 | 0.87879 | 25967 | 15580.2 | 8530.1595 | 113735.46 | 22428.8
39 - Music Building | 2011-03-04 | 105343 | 1828 | 120899 | 74753 | 160998 | 2.1537 | 71607 | 0.95791 | 89391 | 53634.6 | 29364.9435 | 391532.58 | 67264.4
Vet Med Basic Sciences | 2011-04-15 | 259412 | 4248 | 239587.2 | 232758 | 388163 | 1.6677 | 206330 | 0.88646 | 181833 | 109099.8 | 59732.1405 | 796428.54 | 130487.4
Vet Med LAC | 2011-04-15 | 233702 | 1990 | 112236 | 104000 | 150881 | 1.4508 | 77795 | 0.74803 | 73086 | 43851.6 | 24008.751 | 320116.68 | 68384.4
Vet Med SAC | 2011-04-15 |  | 1928 | 108739.2 | 104000 | 140804 | 1.3539 | 73659 | 0.70826 | 67145 | 40287 | 22057.1325 | 294095.1 | 68452.2
Vet Med SOL | 2011-04-15 | 17884 | 212 | 11956.8 | 14769 | 27445 | 1.8583 | 9480 | 0.64189 | 17965 | 10779 | 5901.5025 | 78686.7 | 1177.8
Vet Med Chiller Plant | 2011-04-15 | 23088 | 115 | 6486 | 12643 | 14401 | 1.139 | 7839 | 0.62003 | 6562 | 3937.2 | 2155.617 | 28741.56 | 2548.8
Abbott Power Plant (part.) | 2011-04-15 | 184393 | 177 | 9982.8 | 27298 | 14868 | 0.54466 | 8496 | 0.31123 | 6372 | 3823.2 | 2093.202 | 27909.36 | 6159.6
188 - Turner Student Services | 2009-10-29 | 41264 | 628 | 32593.2 | 24650 | 52164 | 2.1162 | 29453 | 1.1948 | 22711 | 13626.6 | 9489.8368 | 99474.18 | 18966.6
159 - Wohlers Hall | 2009-10-29 | 99550 | 1071 | 64260 | 76140 | 123783 | 1.6257 | 85345 | 1.1209 | 38438 | 23062.8 | 16061.3952 | 168358.44 | 41197.2
CEB (Newmark) | 2011-03-25 | 184393 | 2977 | 167902.8 | 161580 | 316722 | 1.9602 | 224712 | 1.3907 | 92010 | 55206 | 30225.285 | 403003.8 | 112696.8
Water Survey 9 bldgs | 2011-03-28 |  | 1154 | 21603 | 57925 | 97086 | 1.6761 | 55758 | 0.96259 | 41328 | 24796.8 | 13576.248 | 181016.64 | -3193.8
Total |  | 2395301 | 33192 | 2006665.6 | 1832278 | 3038571 |  | 1820327 |  | 1218244 | 730946.4 | 405656.9394 | 5335908.72 | 1275719.2
2 tube eq. fixtures
Estimate watts reduced from 84 to 48
See page 2 fixture consumption estimates
Note on E4: Eva Sweeney: Also included new fixtures and ceiling replacement work

## Eff. Info
Average Wattage of existing fixtures
| Watts | % of exist
T12 Old Magnetic | 77 | 0.4 | 30.8
T12 Magnetic | 72 | 0.15 | 10.8
T12 Electronic | 60 | 0.2 | 12
|  | 0.75 | 53.6
|  |  | 71.4667 | Watts average for T12 existing
New Fixture Wattage |  |  | Fixture
Type | Lamp | Ballast | Total
HP T8 | 32 | BF = .78 | 48
Energy reduction per fixture |  |  | 23.4667
Use Rapid Start Ballast or Programmed Rapid Start for Auto
Ballast Efficacy Factor (BEF) should be at least:
1.47 / 1.52(277V) for two lamps at ballast factor of .88
1.6 for two lamps at ballast factor of .77
1.51/1.54 for two lamps at ballast factor of .71
HP T8s Lamps
GE High Lumen ECO F32T8/XL/SPXxx/HL/ECO
Phillips Advantage ALTO F32/ADV/8xx/ALTO
Sylvania XtremeXPS Ecologic FO32/8xx/XPS/ECO
Productivity
15 minutes per fixture with an overall efficiency of .85 = |  |  |  |  | 3.4 fixtures /Hr (each worker)
General Note: T5s can not be retrofit into existing T12 fixtures

## Ballast-Lamp Data
Ballast Data
Ballast Manufacturer | Part # | # Lamps | Lamp Type | Input watts | BEF %
Universal | B232IUNVEL-A | 2 | T8
Universal | QHE2X32T8UNVISLSC | 2 | T8
Advance | ROP2P32LWSC35M
Advance | ROP3P32LWSC35M
Lamp Data
Lamp Manufacturer | Part # | Initial Lumens | Mean Lumens | Watts | Life @ 3hr/start | Life @ 12hr/start | CRI
Philips T12 "Cool White" | F34/CW/RS/EW/ALTO | 2650 | 2300 | 34 | 20000 |  | 62
Philips Universal (standard T8) | F32T8/TL835/ALTO | 2950 | 2800 | 32 | 20000 | 25000 | 85
Philips Plus (long life) | F32T8/TL835/PLUS/ALTO | 2950 | 2800 | 32 | 30000 | 36000 | 85
Philips Advantage | F32T8/ADV835/ALTO | 3100 | 2950 | 32 | 30000 | 36000 | 85
Philips Energy Advantage | F32T8/ADV835/XEW/LL/ALTO 25 | 2400 | 2280 | 25 | 24000 | 30000 | 85
Philips Energy Advantage | F32T8/ADV835/EW/LL/ALTO 30 | 2850 | 2700 | 30 | 24000 | 30000 | 85
Sylvania Octron | FO32/835 XPS ECO | 3100 | 2945 | 32 | 30000 |  | 85