## Architectural
Project Review
Krannert Center for Performing Arts - Solar System Feasibility Study
Architectural Review Comments
Plan Reviewer: |  | Donna McClure
Comment Number | Drawing or Spec Reference | UIUC Facilities & Services Comment | AE Response
Drawing Comments
|  | It sounds as though we would have a better project if we used a different building… | Agree. We have identified a number of considerations that would suggest an alternate location for a photovoltaic array would be more appropriate.
Specification Comments
General Comments

## Electrical
Project Review
Krannert Center for Performing Arts - Solar System Feasibility Study
Electrical Review Comments
Plan Reviewer: |  | Joseph Youakim - Study
Comment Number | Drawing or Spec Reference | UIUC Facilities & Services Comment | AE Response
Drawing Comments
1 |  | The payback schedule is based on a $0.12 per KWH, however, U of I pays only $0.08 per KWH. So, the payback will extend beyond 25 years which brings the economics of such a project in question. | Agree. Payback does not seem favorable.
Specification Comments
General Comments

## Deferred Maintenance
Project Review: Krannert Center For Performing Arts - Solar System Feasibility Study
Deferred Maintenance Review Comments
Plan Reviewer: |  | John Prince
Comment Number | Drawing or Spec Reference | UIUC Facilities & Services Comment | AE Response
Drawing Comments
Specification Comments
| OPCC | This seems well beyond any currently identifiable fund source. | Agree.
| Page 3 | The electrochromic option needs to be analyzed further per program statement. Real pricing and cost savings must be calculated. Payback should be calculated on the increased cost not the absolute cost of the windows. Note that there are other considerations such as the inability of the existing air conditioning system to keep up with the solar gain, and the UV deterioration of the teak paneling and other building finishes. | We compared energy savings of standard Low E glass and electrochromic glazing against the existing single pane glass. This can be clarified in the text.
| Page 6 | Was the cost of the lightning protection considered in this analysis? Keep in mind that the panel array will be the highest elevation of this building, if not the local area.. Do we need extra protection for sensitive electronic equipment that might be included in these panels? We expect the cost of a fully viable system which must take these elements into consideration. | The cost of lightning protection was not included in the analysis. The photovoltaic system has some surge protection built in, but we agree that additional lightning protection would be prudent.
| Page 6 | KCPA is on a corner of the campus grid. Has it been determined that the grid can handle the output of the collectors in times of low consumption. KCPA is on district heating and cooling and actually has much lower electrical consumption during the summer months due to a reduced performance schedule. | The generated power is not expected to exceed the building's consumption.
| Page 8 | Would the micro-inverters transmit any structural borne noise? | This noise should be negligible when compared to the potential noise from rain / hail. Mitigative measures taken to isolate environmental noise are expected to be sufficient to mitigate any noise from the micro-inverters
| Page 9 | Is the current roof access OSHA compliant? Shouldn't any necessary upgrades be included in the project as the need to access the roof will greatly increase, and shouldn't this be included in the payback analysis? Will altering the roof access alter the acoustic characteristics of the Great Hall? | Roof access is cumbersome and improvements are recommended. Please refer to the updated OPCC in the Phase 2 report on page 8. The recommended modifications to the roof access are not expected to alter the acoustic characteristics of the Great Hall.
| Page 9 | Is it necessary to provide fall protection? Will a hazard be presented to untrained service personnell? We have planned extensive guardrail protection in the North Campus Parking Deck proposal. | The need for fall protection should be further evaluated. At this time it is considered likely that fall protection may not be required due to the extension of the parapets above the roof deck.
| Page B.2, B.4 | It seems both systems have infinite payback. Would it be worthwile to consider a publicly funded incentive, say 30% panel cost? Why are we looking at a ground-mounted system? | Some grant funding may be available, but such funding sources vary with time. We included the comment on the ground mounted array only as a point of consideration, given the signficant cost of ancillary construction that would be requried to prepare the roof structure of the Great Hall to receive a photovoltaic array.
| Page G.2 | What is the life-cycle of the micro-inverters? We ruled them out at NCPD for this reason. | Manufacturer's stated warranty is 25 years.
| Appendix H | There is currently no project to replace the glazing on the hall. Payback calculations must be based on the replacement of the glazing in both scenarios. | Agree. This can be clarified in the report
| Page 2.7 | The acoustic perfection of the Great Hall must be considered as an historically significant interior element. It must be conclusivly determined that this project will not adversely affect it to proceed further. | The AE appreciates the acoustic importance of the Great Hall. This, combined with the complexities and cost of construction resulted in our recommendation not to install photovoltaic cells on the roof of the Great Hall. (Refer to the 3rd paragraph under the Summary of Findings). Extensive acoustic investigation is not within the scope of our services for the Feasibility Study. Note, however, that we have recommended that additional evaluation of the acoustic impact be conducted if this project advances.
| 2-Appendix B | I don't see a relative ranking for these options. Also, for option 2: We have had experience with these housed isolators "short-circuiting" over time. | The options have not been ranked, but are presented only for possible consideration if the project advances.
General Comments